## Case details
Energy Memo: GLA Consultation
Case details
Date of first review: | 13/01/2021
Case Name: | Cambridge Road Estate
Case Number: | 2020/6860
Case Officer: | Emily Leslie
London Borough: | RB Kingston
Application Type (Outline/Hybrid/Detailed): | Hybrid
Applicant: | Cambridge Road RBK LLP
Energy Consultant: | Hodkinson
Document Title: | Energy Statement
Document Date: | 2020-10-01
Development proposals
Use | Floorspace/Number of units
Dwellings | 2170 (452 detailed)
Class E | 290 m2 (detailed)
Sui Generis | 1,395 m2
Community | 1,250 m2 (detailed)

## Pre-application advice
The updated GLA Energy Assessment Guidance provides details on the information that should be provided within the energy assessment to be submitted at stage 1. See link for the latest guidance published in October 2018: https://www.london.gov.uk/what-we-do/planning/planning-applications-and-decisions/pre-planning-application-meeting-service-0 The following targets are in effect for all Stage 1 schemes received by the Mayor as set out in the guidance: Residential – Net zero carbon with at least an on-site 35% reduction in carbon emissions beyond Part L of 2013 Building Regulations. Non-residential – 35% reduction in carbon emissions beyond Part L of 2013 Building Regulations. The zero carbon target will apply to non-domestic developments when the new London Plan is adopted (expected in late 2019). The carbon emission figures should be reported against a Part L 2013 baseline. Carbon emissions for domestic and non-domestic elements of the development should be presented separately. Moreover, carbon emissions for detailed and outline elements should also be presented separately. From January 2019, and until central Government updates Part L with the latest carbon emission factors, applicants are encouraged to use the SAP 10 emission factors for referable applications when estimating CO2 emission performance against London Plan policies. A spreadsheet has been provided for this purpose and the applicant should submit this alongside their application. Applicants will still need to provide an assessment of CO2 performance using SAP 2012 emission factors to enable a comparison to be made. Applicants proposing to only use SAP 2012 emission factors will need to provide a justification for this. Further information on the resulting system carbon factor should be submitted and the methodology used to calculate it. Due to the proposed timing of their application (early 2020), the applicant may be required to meet the new London Plan requirements, which are expected to be adopted at a similar time to the application submission. The applicant proposes to submit a hybrid application, including for a detailed Phase 1 of ~400 homes. The build out of the site will be phased, with phasing affected by the need for decant from existing homes. Additional detail on the phasing plan should be submitted to the GLA. Be Lean Demand Reduction The applicant should commit to meeting Part L 2013 by efficiency measures alone as a minimum for both domestic and non-domestic elements separately. Applicants should note the new draft London Plan Energy Efficiency targets which set out the GLA’s expectation for levels of improvement achievable for new developments: Residential – 10% improvement on 2013 Building Regulations from energy efficiency Non-residential – 15% improvement on 2013 Building Regulations from energy efficiency The applicant proposes to address the new draft London Plan Energy Efficiency targets; this is welcomed. Sample SAP full calculation worksheets (both DER and TER sheets) and BRUKL sheets including efficiency measures alone should be provided to support the savings claimed. These are expected to be submitted for the detailed elements of the site and extrapolated to the outline areas. Information on the development’s total energy demand (MWh/year) for each building use and the total Part L Fabric Energy Efficiency Standard (FEES) should be reported. The applicant proposes to use bespoke psi values for the domestic assessment; they should submit documentation to demonstrate that these are achievable. Cooling and Overheating The domestic overheating checklist, included in the Energy Assessment Guidance, should be completed at pre-application stage and used to identify potential overheating risk and passive responses early in the design process. Evidence should be provided on how the demand for cooling and the overheating risk will be minimised through passive design in line with the Cooling Hierarchy. Dynamic overheating modelling in line with CIBSE Guidance should be carried out (TM59 and TM49 for residential and TM52 and TM49 for non-residential). The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building should be provided and the applicant should demonstrate that the actual building’s cooling demand is lower than the notional. Be Clean Heating Infrastructure The applicant is proposing to connect to the proposed Kingston District Heating network. This is welcomed. Evidence of communication with the relevant parties (i.e. stakeholders, local authority energy officers) should be provided, along with full supporting evidence for the progress in developing the heat network, the network’s capacity to serve the new development, supporting estimates of the CO2 emission factor, installation cost and timescales for connection. The proposed Kingston Heat network will be served by an energy centre at the Thames Water waste water treatment plant that is 300m away from the site. The treatment plant currently releases significant volumes of waste heat into the Hogsmill river at 15-20°C consistently through the year. It is proposed that heat will be transferred to the network by water source heat pumps. Thames Water currently have a CHP which runs on biogas produced on their site, and the expectation is that the electricity produced by the CHP would run the heat pumps. There is also an adjacent crematorium which would contribute to the network. The heat produced for the network is currently estimated to be low carbon; for the Stage 1 application, the applicant will need to support this with detailed calculations based on the current assumptions for the scheme. The Cambridge Road Estate is seen as a key customer that would provide the network with the customers required to catalyse the proposed heat network, and the proposed connection would be across a local authority owned cemetery and is therefore the technical connection challenges are considered minor. The heat network is planned to be later extended to Kingston Town Centre, and there are other local developments coming through that may have an interest in connecting; modular heat pumps will be added as required. It is anticipated that the heat network temperature provided will be sufficient to allow the Cambridge Road Estate to connect with without additional top-up. Detailed information on the operation of the system and its interaction with the CRE should be submitted as part of the Stage I application. The proposed district heating scheme will be taken forward as a Joint Venture (JV) by Royal Borough of Kingston and Thames Water, with the Cambridge Road Estate as a key partner, and it is considered to have significant political support. The JV are currently tendering for a detailed feasibility study for the scheme, and this is expected to be completed in December 2019. This would be followed with detailed design and commercialisation work through 2020. Funding for the work is planned to come from sources including HNIP (application due in December). Any updated information associated with the DHN will be expected to be submitted to the GLA as additional evidence. The applicant should provide an update on progress with the Kingston Heat network and the feasibility study. An update has been provided confirming that further discussions have been held with the key stakeholders. Timing have been further refined with a proposed review date being pushed back until later in the development programme to give the best opportunity for a connection agreement. The GLA will seek for a condition to be attached to an approval granted for this scheme which would set out the process for obtaining reasonable confirmations on the viability of a connection to the RBK DEN and the timescales required to implement the alternative LZC option should a connection not be viable. It is proposed that temporary gas boilers will be provided on-site in Phase 1 to supply the site-wide heat network prior to the heat network connection. Sufficient space will be allowed for in the Phase 1 plant room for the installation of boilers to supply the whole site for resilience. These will be installed in a modular manner and the expectation is that the boilers could be adopted by the Kingston heat network and the majority of the space allowance will be converted to other uses if and when the network connection is made. The site should be served by a single energy centre and the applicant should commit to providing a site wide heating network where all buildings/uses on site will be connected; relevant drawings/schematics for the energy centre and the site-wide network should be provided. The applicant should outline how a site-wide network will be provided for the initial phases and developed over-time. There appear to be three energy centres proposed, and the applicant will be required to demonstrate any constraints to a site-wide network and that they have minimised the number of energy centres. The applicant has updated their approach to try an utilise only a single energy centre for either the preferred and the alternative scenario. This is supported. The applicant should provide information confirming that the development is future proofed for connection to wider district networks now or in the future. Be Green Renewable Energy The GLA expects all major development proposals to maximise on-site renewable energy generation. This is regardless of whether the 35% on-site target has already been met through earlier stages of the energy hierarchy. Solar PV should be maximised. It is noted that living roofs are proposed to much of the roof area, which is welcomed. The applicant should consider the potential for biosolar roofs which can provide for the benefits of living roofs and PV. It is expected that rationalised roof layouts will be provided including for all required uses, including PV. A plan showing the proposed location of the installation should be provided and the applicant should demonstrate that the roof’s potential has been maximised for the installation. The applicant has raise the issue that roof availability under the alternative scenario, which utilises ASHPs, will be significantly reduced. They are required to present two options for the outline and future reserved matters applications to demonstrate that PV has been maximised for each scenario in line with the previous pre-app comments on PV allocation. The applicant should consider that a planning condition will be required which will require further measures to be provided if the proposed connection to the Kingston district heating network is not achieved within an agreed timescale. It is expected that this would be an on-site low carbon heating source designed in a later phase that would be designed to serve the whole site-wide network. However, the applicant has suggested that there may be limitations to this. They should present their preferred alternative measures, and clearly outline any constraints they believe exist to GLA’s preferred alternative option of an on-site low carbon heat source. In line with the energy assessment guidance, an on-site low carbon alternative would be the GLA’s expectation, prior to the consideration of contribution to a carbon offset fund. The applicant has reaffirmed the preferred strategy as being a connection to the RBK DEN and given further details of the proposed alternative strategy, which at this stage is acceptable to the GLA. As mentioned above a planning condition should be agreed to secure a reasonable time scale for establishing a connection to the RBK DEN to replace the temporary gas boiler solution as well as ensuring that if this connection can not be established then the alternative energy strategy will be delivered in an appropriate timeframe after the developments completion. Carbon Offsetting Applicants are expected to maximise carbon emission reductions on-site. Where it is clearly demonstrated that no further carbon savings can be achieved but the site still falls short of the carbon reduction targets, applicants are required to make a cash-in-lieu contribution to the relevant boroughs’ carbon offset fund using the boroughs’ carbon offset price. Energy strategies should provide a calculation of the shortfall in carbon emissions and evidence of discussions with the borough agreeing the offsetting approach. Monitoring The energy strategy should include information on how the building’s energy performance will be monitored post-construction to enable occupants to monitor and reduce their energy use.

## Energy Comments
Comment No. | GLA Stage I | Applicant's Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response | Applicant's Post Stage I response | GLA Post Stage I response
| Date: 13/01/2021 | Date: 05/02/2021 | Date: 02/03/21 | Date: 16/03/2021 | Date: 25/03/21 | Date: | Date: 01/04/21 | Date: 19/04/2021 | Date: 27/04/21 | Date: 28/04/21 | Date: 06/05/21 | Date: 07/05/21 | Date: 06/05/21
General compliance comments
Be Lean
Overheating
Be Green
14 | The applicant is proposing to install 55 kWp of Photovoltaic (PV) panels for the detailed element with an estimated output of 41,000 kWh of electricity generation. A further 210 kWp has been estimated for the outlined element. A roof layout has been provided; however, the applicant should submitted a more detailed layout for the detailed elements which shows all proposed roof uses and panel locations to demonstrate that the roof’s potential for a PV installation has been maximised. This information will be required for all future reserved matters applications. | Thank you for confirming acceptability. For reference detailed PV layout can be found in Appendix L of the Energy Statement and further the attached drawings which focus on Phase 1. Drawings 503-PTA-BZ-ZZ-DR-A-1302_S4-PL1, 503-PTA-CZ-ZZ-DR-A-1302_S4-PL1, 503-PTA-EZ-ZZ-DR-A-1302_S4-PL1 show how the Phase 1 roofs are proposed to be used. | The roof layout confirms that there are areas of high roofs proposed for biosolar roofs, which are welcomed, and other high roofs proposed for green roofs but not PV. Clarification should be provided regarding the constraints to making all the areas proposed for green roofs as biosolar roofs. The applicant is required to demonstrate that the roof’s potential for a PV installation has been maximised, and they should reconsider the PV provision. This item is outstanding. | There are several constraints explaining why biosolar is not applied to the lower roofs and explain why PV is maximised: 1) Expected solar yield will be lower due to self shading from other towers in the block arrangement. 2) Expected solar yield will be lower due to shading from other blocks in the masterplan. 3) Expected solar yield will be low due to orientation (e.g. North Facing). 4) The green roof is used for biodiversity (bats, birds, etc) which could foul PV | The clarifications are welcomed. A more specific response is required for the higher green roofs not proposed for PV. Where solar shading levels are cited, solar insolation levels should be submitted. The applicant is required to demonstrate that the roof’s potential for a PV installation has been maximised, and they should reconsider the PV provision. This item is outstanding. | Based on the design developed for planning, PV provision has been maximised on perceived unshaded roof spaces. The requested information would not be available at this stage as the design will not have sufficiently progressed. Further, some roofs will be primarily used for ecological purposes which PV may have an impact upon. At this stage the applicant will accept to submit further detail demonstrating that PV has been maximised on completion of detailed design. | The applicant has stated that more detailed information to support the further PV provision is not avialable at this stage. They should be conditioned to demostrate that PV has been maximised prior the detailed elements of this application commencing above ground works. The proposed PV arrays should be supported by irradiance anaylsis, detailed roof use drawings and technial viability assessment of including PV on any ecological enhancement roof areas. | Accepted, propose condition: Before completion of each phase, demonstrate PV has been maximised based on technical viability and does not negate ecological enhancements. | Proposed amendment to condition wording in red text: Before commencing above ground works for each phase, the applicant is required to demonstrate to the borough, in consultation with GLA, that PV has been maximised to all areas, including green/brown roofs, based on technical feasbility and does not significantly negate ecological enhancements. This should be supported by irradiance analysis and the submission of a detailed roof layout clearly labelling any constraints to additional PV. | We’d be happy to agree to the PV condition but with the irradiance analysis omitted | Assessing the technical feasibility of PV is likely to require quantification of solar irradiance / overshading for some areas. This item could be caveated with "where relevant" to allow a degree of flexibility. Proposed amendment to condition wording in blue text: Before commencing above ground works for each phase, the applicant is required to demonstrate to the borough, in consultation with GLA, that PV has been maximised to all areas, including green/brown roofs, based on technical feasbility and does not significantly negate ecological enhancements. This should be supported by irradiance analysis (where relevant) and the submission of a detailed roof layout clearly labelling any constraints to additional PV. | Condition accepted | This will be addressed through a condition.
Carbon performance and offsetting
18 | The applicant has confirmed that £299,271 will be paid into the borough’s offset fund, equivalent to 166 tonnes of CO2 per annum for the detailed element of the scheme. The outline element has been estimated to need a £1,127,085 offset amount; however, this should be confirmed by the upcoming reserved matters. It should also be noted that the £95/tonne and non-domestic zero carbon requirement would be expected should the Published London Plan be formally adopted within the determination period of this hybrid application. | Noted | The draft s106 agreement should be submitted when available to evidence the carbon offsetting arrangement. This item is outstanding. | Meaningful discussions regarding the s106 legal agreement are yet to commence. However, the Draft s106 will be shared with the GLA as part of the Stage 2 referral and available for GLA Officers to review prior to Planning Permission being granted. | The draft s106 agreement should be submitted when available to evidence the carbon offsetting arrangement. This item is outstanding. | Discussions regards the s106 are due to commence with RBK on the 6th April 2020. We can share draft obligation in due course. | This is due to be submitted in due course and is currently still outstanding. | Correct. | The draft s106 agreement should be submitted when available to evidence the carbon offsetting arrangement. This item is outstanding. |  | The draft s106 agreement should be submitted when available to evidence the carbon offsetting arrangement. This item is outstanding. | No response. | The draft s106 agreement (or other correspondence from the borough) should be submitted when available to evidence the carbon offsetting arrangement. This item is outstanding.
Whole Life-Cycle Carbon Assessment
Be Seen' Energy Monitoring
Other points
Move resolved comments under this section
1 | The energy strategy is generally compliant with the London Plan policies however, the applicant is required to submit the additional information, which has been requested below. | Thank you for confirming acceptability. | This item will be addressed through response to all other items. Nothing further required here.
2 | For the purposes of this assessment, the applicant will be estimating the CO2 emission performance against London Plan policies using the SAP 10 emissions factors. This is supported. | Thank you for confirming acceptability. | Nothing further required.
3 | The applicant has submitted the pdfs of the GLA’s Carbon Emission Reporting spreadsheet, which has been developed to allow the use of the updated SAP 10 emission factors alongside the SAP 2012 emission factors. Please can they also submit the excel file for the development. | Please find excel file attached | Nothing further required.
4 | Based on the information provided, the domestic element of the proposed detailed element of the development is estimated to achieve a reduction of 60 tonnes per annum (13%) in regulated CO2 emissions compared to a 2013 Building Regulations compliant development. For each reserved matters applications detailed calculations should be provided to demonstrate that the outline elements achieve the 13% reduction reported and as a minimum ensure that the 10% reduction required by London Plan policy is achieved. | We agree with the GLA that a minimum 10% in regulated CO2 emissions compared to a 2013 Building Regulations compliant development should be required here and this is what should be conditioned. It should not be expected for the masterplan to commit to 13%. This is a detail which is not covered at this stage. | This will be addressed by a condition to achieve the 10% reduction from energy efficiency required by London Plan Be Lean policy for reserved matters applications.
5 | Based on the information provided, the non-domestic element of the proposed detailed element of the development is estimated to achieve a reduction of 3 tonnes per annum (20%) in regulated CO2 emissions compared to a 2013 Building Regulations compliant development. For each reserved matters applications detailed calculations should be provided to demonstrate that the outline elements achieve the 15% reduction required by London Plan policy. | We agree with the GLA that a minimum 15% in regulated CO2 emissions compared to a 2013 Building Regulations compliant non-domestic units should be required here and this is what should be conditioned. It should not be expected for the masterplan to commit to 20%. This is a detail which is not covered at this stage. | This will be addressed by a condition to achieve the 15% reduction from energy efficiency required by London Plan Be Lean policy for reserved matters applications.
8 | The area weighted average (MJ/m2) and total (MJ/year) cooling demand for the actual and notional building has been provided and the applicant should has demonstrated that the actual building’s cooling demand is lower than the notional. | Thank you for confirming acceptability. | Nothing further required.
10 | The applicant has provided a commitment that the development is designed to allow future connection to a district heating network. Drawings demonstrating how the site is to be future-proofed for a connection to a district heating network have been provided detailing all required information. | Thank you for confirming acceptability. | Nothing further required.
11 | The applicant is proposing a site-wide heat network supplied by a centralised energy centre. It has been confirmed that all apartments and non-domestic building uses will be connected to the heat network. A drawing showing the route of the heat network linking all buildings on the site has been provided alongside a drawing indicating the floor area, internal layout and location of the energy centre. | Thank you for confirming acceptability. | Nothing further required.
16 | The applicant has provided the relevant modelling output sheets (i.e. TER, DER, BRUKL) for the all stages of the energy hierarchy. | Thank you for confirming acceptability. | Nothing further required.
17 | The carbon dioxide savings exceed the on-site target set within the London Plan for domestic and non-domestic uses. | Thank you for confirming acceptability. | Nothing further required.
19 | The applicant has submitted a WLC assessment which will be reviewed separately; comments will be provided. The WLC assessment should follow the GLA WLC guidance and reporting template (https://www.london.gov.uk/what-we-do/planning/implementing-london-plan/planning-guidance/whole-life-cycle-carbon-assessments-guidance-pre-consultation-draft). Applicants will also be conditioned to submit a post-construction assessment to report on the development’s actual WLC emissions. | Noted | WLC is reviewed separately. Nothing further required here.
25 | The applicant has completed and submit the Good Homes Alliance Early Stage Overheating Risk Tool. | No comment | Nothing further required.
6 | The applicant should consider and minimise the estimated energy costs to occupants and outline how they are committed to protecting the consumer from high prices. This should cover the parameters set out in the guidance and include a confirmation of the quality assurance mechanisms that will be considered as part of the strategy. | The scheme has addressed this by ensuring that the base build will be better than Building Regulations. The assessment process for considering connection to the wider heat network or having a stand alone network will include cost as a factor. The Royal Borough of Kingston Upon Thames are aware of this principle and are progressing with it in mind. | Further detail is required on the quality assurance mechanisms that will be considered as part of the strategy. This item is outstanding. | The quality assurance mechanism that will be considered as a part of the strategy will be to ensure that the onsite heat networks are designed in line with CIBSE CP1. In additional to earlier comments the benchmarks for heat prices are what can be achieved through the onsite strategy & the Heat Trust cost comparator. | The clarifications are welcomed. Nothing further required.
15 | As a alternative/backup strategy for the masterplan, heat pumps are being proposed in the form of a (centralised) hybrid ASHP system. Information on the heat pump proposals have been provided; however, should this strategy become the proposed approach then further information on the heat pumps would be requested as part of any reserved matters applications. This would include a dynamic calculation of the SCOP for the proposed heat pump arrangement, detailed roof plans of the ASHP plant and confirmation of how the ASHP outputs will be interfaced with the proposed site heat network. | Please see comment 9 with respect to timing and provision of information during future Reserved Matters Application. Information will be provided in line with Part L calculation if required. | This will be addressed by a condition to provide relevant heat pump details as part of reserved matters applications where necessary. | This should not be conditioned as a part of the RMA. As discussed in GLA's post stage 1 response to comment 9 the use of heat pumps is directly linked to the connection to the offsite heat network. The mechanism proposed in comment 9 with respect to our comments is the appropriate approach. | This has been incorporated into item 9. Nothing further required here.
7 | The results of the Dynamic Overheating Analysis, using the CIBSE TM59 methodology, demonstrate that compliance under the DSY 1 scenario can be achieved for all tested rooms assuming a g-value of 0.45, reflective internal blinds and enhanced ACH in acoustically or air quality constrained rooms. The applicant has also investigate the risk of overheating using the DSY 2 & 3 weather files. The applicant should confirm that the required reflective blinds will be included in the base build and demonstrate that the blinds do not interfere with the effective opening area of windows. The applicant has outlined that the window opening strategy for the rooms which have acoustic and air quality constraints is considered acceptable by the acoustician and A consultants. The applicant references an rate of 4 ACH from the mechanical ventilation strategy. They should confirm if this is possible with the MVHR performance outlined in the Energy Statement. | The applicant has confirmed that blinds will be considered where required to prevent overheating. The ventilation rate has been confirmed as achievable by the mechanical designers base on planning information. The units would have a dedicated MVHR system for background ventilation and a dedicated purge system for overheating. | The applicant should confirm that the required reflective blinds will be included in the base build and demonstrate that the blinds do not interfere with the effective opening area of windows. They have currently only stated that these will be considered. Further detail should be provided on the dedicated purge system for overheating. The applicant should commit to providing guidance to occupants on minimising the dwelling overheating risk in line with the cooling hierarchy. This item is outstanding. | The applicant confirms that blinds will be included in the base build where it is not possible for an alternative strategy to achieve a similar outcome. The additional purge ventilation is not expected across the entire development. It impacts several units which are considered to have high external noise levels. These units are expected to have an MVHR units and a dedicated mechanical purge vent. These two units would work to boost ventilation to 4ACh when required. The applicant confirms that guidance will be provided to occupants on minimising dwelling overheating risks. | The clarifications are welcomed. The applicant should confirm whether the dedicated mechanical purge vent system has been included for in the energy modelling. This item is outstanding. | The energy modelling has been based on utilising the SAP methodology in line with GLA requirements. The regulated calculation methodology does not allow entry for more than one ventilation system. Purge ventilation systems are expected to have low energy consumption as they would not be utilised all the time. | The applicant has confirmed that the SAP modelling has been based on the most signifnant mechnical ventilation system of those proposed to capture the energy consumption most accurately. This is accepted and nothign further is required. | n/a
9 | The applicant has identified the potential RBKUT DEN within the vicinity of the development and is proposing to connect to the network. Connection to the network should continue to be prioritised and details of any initial agreements should be provided (it is noted that this may be conducted internally at RBKUT). Information provided within the statement confirms that the network has the capacity to serve the new development and the carbon intensity and initial estimates of cost of heat have been provided. As the DEN carbon intensity is calculated using SAP 10 carbon emission factors there is no requirement for a decabonisation plan for the network. The applicant should confirm the timescales for the development phasing. As the GLA wishes to understand the timescale between the first phase being completed to a year before the final phase being completed. Typically the GLA considers 5 years as the maximum period for use of temporary gas boiler plant. The applicant has confirmed that connection will be prioritised but have made provision for a backup ASHP strategy should a connection not be achieved 1 year prior to the completion of the final development phase. Interim gas boilers are proposed until a connection is established. A planning condition should be drafted to secure the connection to the RBKUT DEN. The development should, prior to the final reserved matters energy statement being submitted, fully detail the proposed connection to the RBKUT DEN, including details of connection agreement, final timescales for the connection, pipework routing drawings and final heat carbon intensity. Should any of this information differ to previous reserved matters applications or this outline application then final carbon offsetting agreements for the masterplan should be revised accordingly. Should a connection to the RBKUT DEN not be viable at this stage then the applicant should submit a revised masterplan energy strategy based on the alternative ASHP gas boiler hybrid strategy and demonstrate that compliance with all London Plan policies are maintained as well as provide a revised carbon offsetting amount for the masterplan. | The timescale for the development is dependant on achieving vacant possession, therefore the exact timeline is uncertain. However works on the first phase which includes the energy centre are expected this year, on the basis of consent. For clarity, the temporary gas boilers would be in place until the energy centre is built. The energy centre is in Phase 1. It is considered that the plant in the energy centre will then provide heat until connection to the RBKUT DEN or alternative strategy is put in place. At this point the plant in the energy centre will be utilised as back up only. Though the development team and RBKUT DEN are in continual discussions the Reserved Matters Application, RBKUT DEN and development build timelines are unlikely to be in alignment. The proposal of linking the energy strategy with the final Reserved Matters Application would add a risk of forcing a heating infrastructure option which is not the GLA's priority. It is therefore suggested that alternative methods such as a planning condition linking to completing homes in the final phase is considered. This is to provide the greatest possible time for the connection to be made. | The clarifications are welcomed, and the applicant's preference regarding the planning condition are noted. It is accepted that the condition references the completion of homes in the final phase rather than the reserved matters application. However, this should also reference "5 years from the occupation of the first home", as an alternative trigger point, should the final homes not be completed within 5 years of the first home. When the condition is triggered, if connection to the RBKUT DEN has been made, the details previously suggested should be submitted for review. If connection has not been made by the trigger point, the current status of the network and prospect for future connection should be established and reported to the borough and GLA for comment. At this point, unless it is agreed that there remains a good prospect of a connection to the RBKUT being achieved within a suitable timescale (with a further trigger point and submission to be agreed at the time), the alternative ASHP gas boiler hybrid energy strategy should be installed, with a submission made to demonstrate that compliance with all London Plan policies are maintained as well as provide a revised carbon offsetting amount for the masterplan. This item is outstanding. | We propose: Within 5 years of occupation of the first home, an updated energy strategy should be submitted to the Local Planning Authority and GLA. This should include an update on the potential connection to the RBKUT DEN and the programme for connecting the proposed development to the district energy network. If a connection to the district energy network is still feasible and likely after 5 years then annual updates should be provided to the Local Planning Authority and GLA to help monitor implementation of the preferred energy strategy. If connection to the RBKUT DEN is achievable then details of connection agreement, final timescales for the connection, pipework routing drawings and final heat carbon intensity should be submitted to the Local Planning Authority and GLA prior to occupation of the dwellings within the final Phase or at an earlier point if possible. Should a connection to the RBKUT DEN not be viable at any stage of the proposed development then the applicant should submit a revised masterplan energy strategy based on the alternative ASHP gas boiler hybrid strategy and demonstrate compliance with the relevant London Plan policies and carbon reductions / carbon offsetting secured as part of the outline planning permission and subsequent reserved matters applications. The energy strategy must be fixed and implemented prior to occupation of the dwellings within the final Phase. | The proposed condition is broadly welcomed to secure this issue. Amendments are proposed in red text: Within 5 years of occupation of the first home, an updated energy strategy should be submitted to the Local Planning Authority and GLA. This should include an update on the potential connection to the RBKUT DEN and the programme for connecting the proposed development to the district energy network. If a connection to the district energy network is agreed by the applicant, the Local Planning Authority and GLA to still be feasible and likely after 5 years then annual updates should be provided to the Local Planning Authority and GLA to help monitor implementation of this preferred energy strategy. If connection to the RBKUT DEN is achievable then details of connection agreement, final timescales for the connection, pipework routing drawings and final heat carbon intensity should be submitted to the Local Planning Authority and GLA prior to occupation of the dwellings within the final Phase or at an earlier point if possible. Should a connection to the RBKUT DEN not be feasible at any stage of the proposed development then the applicant should submit relevant information to demonstrate this to the Local Planning Authority and GLA. Should the Local Planning Authority and GLA approve this relevant information, the applicant should submit a revised masterplan energy strategy based on the alternative ASHP gas boiler hybrid strategy, submit full technical details for the proposed heat pumps, and demonstrate compliance with the relevant London Plan policies and carbon reductions / carbon offsetting secured as part of the outline planning permission and subsequent reserved matters applications. The energy strategy must be fixed and implemented prior to occupation of the dwellings within the final Phase. | The proposed condition is broadly welcomed to secure this issue. Amendments are proposed in red text: Within 5 years of occupation of the first home, an updated energy strategy should be submitted to the Local Planning Authority and GLA. This should include an update on the potential connection to the RBKUT DEN and the programme for connecting the proposed development to the district energy network. If a connection to the district energy network is agreed by the applicant, the Local Planning Authority and GLA to still be feasible and likely after 5 years then annual updates should be provided to the Local Planning Authority and GLA to help monitor implementation of this preferred energy strategy. If connection to the RBKUT DEN is achievable then details of connection agreement, final timescales for the connection, pipework routing drawings and final heat carbon intensity should be submitted to the Local Planning Authority and GLA prior to occupation of the dwellings within the final Phase or at an earlier point if possible. Should a connection to the RBKUT DEN not be feasible and viable at any stage of the proposed development then the applicant should submit relevant information to demonstrate this to the Local Planning Authority and GLA. Should the Local Planning Authority and GLA approve this relevant information, the applicant should submit a revised masterplan energy strategy based on the alternative ASHP gas boiler hybrid strategy, submit full technical details for the proposed heat pumps, and demonstrate compliance with the relevant London Plan 2021 policies, as published in March 2021, and carbon reductions / carbon offsetting secured as part of the outline planning permission and subsequent reserved matters applications, applying on the calculation methodology utilised for the outline consent. The energy strategy must be fixed and implemented prior to occupation of the dwellings within the final Phase. | The applicant has provided revised condition wording. This has been reviewed and is acceptable to the GLA energy team. Condition wording to be include within any decision documentation for this application. | n/a
20 | The applicant should provide a commitment that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This will be secured through suitable legal wording. The first submission of the planning stage data should be provided to the GLA through the be seen reporting spreadsheet within four weeks of planning approval. | Noted, details are also provided in section 8 of the Energy Statement. | The applicant should provide a commitment that the development will be designed to enable post construction monitoring and that the information set out in the ‘be seen’ guidance is submitted to the GLA’s portal at the appropriate reporting stages. This item is outstanding. This will be secured through suitable legal wording. | Accepted. | This will be secured through suitable legal wording. | Accepted. | Nothing further requried. | n/a

## CO2 performance
Domestic (detailed)
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 450
Energy Efficiency | 390 | 60 | 13.33%
CHP | 176 | 214 | 47.56%
Renewable energy | 166 | 10 | 2.222%
Total |  | 284 | 63.11%
Non-domestic (detailed)
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 16
Energy Efficiency | 13 | 3 | 18.75%
CHP | 13 | 0 | 0%
Renewable energy | 9 | 4 | 25%
Total |  | 7 | 43.75%
Outline scheme
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 1698
Energy Efficiency | 1470 | 228 | 13.43%
CHP | 663 | 807 | 47.53%
Renewable energy | 626 | 37 | 2.179%
Total |  | 1072 | 63.13%
Non-domestic (outline)
SAP 10 | Total residual regulated CO2 emissions | Regulated CO2 emissions reductions
| (tonnes per annum) | (tonnes per annum) | (per cent)
Baseline i.e. 2013 Building Regulations | 16
Energy Efficiency | 13 | 3 | 18.75%
CHP | 13 | 0 | 0%
Renewable energy | 9 | 4 | 25%
Total |  | 7 | 43.75%